## OpenTherm v2.2
Register	R/W	DataType	Description
0	RW	LB(flag8)/HB(flag8)	Master and Slave Status flags
1	W	f8.8	Control setpoint ie CH water temperature setpoint (°C)
2	W	flag8/u8	Master Configuration Flags / Master MemberID Code
3	R	flag8/u8	Slave Configuration Flags / Slave MemberID Code
4	W	u8/u8	Remote Command
5	R	flag8	Application-specific fault flags and OEM fault code
6	R	flag8	Remote boiler parameter transfer-enable & read/write flags
7	W	f8.8	Cooling control signal (%)
8	W	f8.8	Control setpoint for 2e CH circuit (°C)
9	R	f8.8	Remote override room setpoint
10	R	u8	Number of Transparent-Slave-Parameters supported by slave
11	RW	u8	Index number / Value of referred-to transparent slave parameter.
12	R	u8	Size of Fault-History-Buffer supported by slave
13	R	u8	Index number / Value of referred-to fault-history buffer entry.
14	W	f8.8	Maximum relative modulation level setting (%)
15	R	u8	Maximum boiler capacity (kW) / Minimum boiler modulation level (%)
16	W	f8.8	Room Setpoint (°C)
17	R	f8.8	Relative Modulation Level (%)
18	R	f8.8	Water pressure in CH circuit (bar)
19	R	f8.8	Water flow rate in DHW circuit. (litres/minute)
20	RW	u8	Day of Week and Time of Day
21	RW	u8	Calendar date
22	RW	u16	Calendar year
23	W	f8.8	Room Setpoint for 2nd CH circuit (°C)
24	W	f8.8	Room temperature (°C)
25	R	f8.8	Boiler flow water temperature (°C)
26	R	f8.8	DHW temperature (°C)
27	R	f8.8	Outside temperature (°C)
28	R	f8.8	Return water temperature (°C)
29	R	f8.8	Solar storage temperature (°C)
30	R	f8.8	Solar collector temperature (°C)
31	R	f8.8	Flow water temperature CH2 circuit (°C)
32	R	f8.8	Domestic hot water temperature 2 (°C)
33	R	s16	Boiler exhaust temperature (°C)
48	R	s8	DHW setpoint upper & lower bounds for adjustment (°C)
49	R	s8	Max CH water setpoint upper & lower bounds for adjustment (°C)
50	R	s8	OTC heat curve ratio upper & lower bounds for adjustment
56	RW	f8.8	DHW setpoint (°C) (Remote parameter 1)
57	RW	f8.8	Max CH water setpoint (°C) (Remote parameters 2)
58	RW	f8.8	OTC heat curve ratio (°C) (Remote parameter 3)
100	R	flag8	Function of manual and program changes in master and remote room setpoint.
115	R	u16	OEM-specific diagnostic/service code
116	RW	u16	Number of starts burner
117	RW	u16	Number of starts CH pump
118	RW	u16	Number of starts DHW pump/valve
119	RW	u16	Number of starts burner during DHW mode
120	RW	u16	Number of hours that burner is in operation (i.e. flame on)
121	RW	u16	Number of hours that CH pump has been running
122	RW	u16	Number of hours that DHW pump has been running or DHW valve has been opened
123	RW	u16	Number of hours that burner is in operation during DHW mode
124	W	f8.8	The implemented version of the OpenTherm Protocol Specification in the master.
125	R	f8.8	The implemented version of the OpenTherm Protocol Specification in the slave.
126	W	u8	Master product version number and type
127	R	u8	Slave product version number and type

## OTv22
Register	R/W	DataObject	DataType	Description	SubClass
0	R -	Status	flag8 / flag8	Master and Slave Status flags.	OT_reg_0
1	- W	TSet	f8.8	Control setpoint ie CH water temperature setpoint (°C)	OT_f88_C
2	- W	M-Config / M-MemberIDcode	flag8 / u8	Master Configuration Flags / Master MemberID Code	OT_reg_2
3	R -	S-Config / S-MemberIDcode	flag8 / u8	Slave Configuration Flags / Slave MemberID Code	OT_reg_3
4	- W	Command	u8 / u8	Remote Command	OT_u8u8
5	R -	ASF-flags / OEM-fault-code	flag8 / u8	Application-specific fault flags / OEM fault code	OT_reg_5
6	R -	RBP-flags	flag8 / flag8	Remote boiler parameter transfer-enable & read/write flags	OT_reg_6
7	- W	Cooling-control	f8.8	Cooling control signal (%)	OT_f88_p
8	- W	TsetCH2	f8.8	Control setpoint for 2e CH circuit (°C)	OT_f88_C
9	R -	TrOverride	f8.8	Remote override room setpoint	OT_f88_C
10	R -	TSP	u8 / u8	Number of Transparent-Slave-Parameters supported by slave	OT_u8u8
11	R W	TSP-index / TSP-value	u8 / u8	Index number / Value of referred-to transparent slave parameter.	OT_u8u8
12	R -	FHB-size	u8 / u8	Size of Fault-History-Buffer supported by slave	OT_u8u8
13	R -	FHB-index / FHB-value	u8 / u8	Index number / Value of referred-to fault-history buffer entry.	OT_u8u8
14	- W	Max-rel-mod-level-setting	f8.8	Maximum relative modulation level setting (%)	OT_f88_p
15	R -	Max-Capacity / Min-Mod-Level	u8 / u8	Maximum boiler capacity (kW) / Minimum boiler modulation level(%)	OT_reg_15
16	- W	TrSet	f8.8	Room Setpoint (°C)	OT_f88_C
17	R -	Rel.-mod-level	f8.8	Relative Modulation Level (%)	OT_f88_p
18	R -	CH-pressure	f8.8	Water pressure in CH circuit (bar)	OT_reg_18
19	R -	DHW-flow-rate	f8.8	Water flow rate in DHW circuit. (litres/minute)	OT_reg_19
20	R W	Day-Time	u3 / u5 / u8	Day of Week and Time of Day	OT_reg_20
21	R W	Date	u8 / u8	Calendar date	OT_u8u8
22	R W	Year	u16	Calendar year	OT_u16
23	- W	TrSetCH2	f8.8	Room Setpoint for 2nd CH circuit (°C)	OT_f88_C
24	- W	Tr	f8.8	Room temperature (°C)	OT_f88_C
25	R -	Tboiler	f8.8	Boiler flow water temperature (°C)	OT_f88_C
26	R -	Tdhw	f8.8	DHW temperature (°C)	OT_f88_C
27	R -	Toutside	f8.8	Outside temperature (°C)	OT_f88_C
28	R -	Tret	f8.8	Return water temperature (°C)	OT_f88_C
29	R -	Tstorage	f8.8	Solar storage temperature (°C)	OT_f88_C
30	R -	Tcollector	f8.8	Solar collector temperature (°C)	OT_f88_C
31	R -	TflowCH2	f8.8	Flow water temperature CH2 circuit (°C)	OT_f88_C
32	R -	Tdhw2	f8.8	Domestic hot water temperature 2 (°C)	OT_f88_C
33	R -	Texhaust	s16	Boiler exhaust temperature (°C)	OT_reg_33
48	R -	TdhwSet-UB / TdhwSet-LB	s8 / s8	DHW setpoint upper & lower bounds for adjustment (°C)	OT_s8s8_C
49	R -	MaxTSet-UB / MaxTSet-LB	s8 / s8	Max CH water setpoint upper & lower bounds for adjustment (°C)	OT_s8s8_C
50	R -	Hcratio-UB / Hcratio-LB	s8 / s8	OTC heat curve ratio upper & lower bounds for adjustment	OT_s8s8
56	R W	TdhwSet	f8.8	DHW setpoint (°C) (Remote parameter 1)	OT_f88_C
57	R W	MaxTSet	f8.8	Max CH water setpoint (°C) (Remote parameters 2)	OT_f88_C
58	R W	Hcratio	f8.8	OTC heat curve ratio (°C) (Remote parameter 3)	OT_f88_C
100	R -	Remote override function	u8 / flag8	Function of manual and program changes in master and remote room setpoint.	OT_reg_100
115	R -	OEM diagnostic code	u16	OEM-specific diagnostic/service code	OT_u16
116	R W	Burner starts	u16	Number of starts burner	OT_u16
117	R W	CH pump starts	u16	Number of starts CH pump	OT_u16
118	R W	DHW pump/valve starts	u16	Number of starts DHW pump/valve	OT_u16
119	R W	DHW burner starts	u16	Number of starts burner during DHW mode	OT_u16
120	R W	Burner operation hours	u16	Number of hours that burner is in operation (i.e. flame on)	OT_u16
121	R W	CH pump operation hours	u16	Number of hours that CH pump has been running	OT_u16
122	R W	DHW pump/valve operation hours	u16	Number of hours that DHW pump has been running or DHW valve has been opened	OT_u16
123	R W	DHW burner operation hours	u16	Number of hours that burner is in operation during DHW mode	OT_u16
124	- W	OpenTherm version Master	f8.8	The implemented version of the OpenTherm Protocol Specification in the master.	OT_f88
125	R -	OpenTherm version Slave	f8.8	The implemented version of the OpenTherm Protocol Specification in the slave.	OT_f88
126	- W	Master-version	u8 / u8	Master product version number and type	OT_u8u8
127	R -	Slave-version	u8 / u8	Slave product version number and type	OT_u8u8